## Slide 1
2- PIPE FLOW PROBLEMS
In pipe flow, there are three types of problems pertaining to determination of:
(a) the nodal head
(b) the discharge through a pipe link
(c) the pipe diameter. Problems
2.1- Nodal Head Problem
In the nodal head problem, the known quantities are L, D, hL, Q, ε, υ and kf.
So, the nodal head h2 (as shown in the Figure ) is obtained as:

## Slide 2
2.2- Discharge Problem
For a long pipeline, form losses can be neglected. Thus, in this case the known quantities are L, D, hf, ε, and υ. Swamee and Jain (1976) gave the following solution for turbulent flow through such a pipeline:
For laminar flow, the Hagen–Poiseuille equation gives the discharge as:
Swamee and Swamee (2008) gave the following equation for pipe discharge that is valid under laminar, transition, and turbulent flow conditions:

## Slide 3
2.3- Diameter Problem
Diameter Problem In this problem, the known quantities are L, hf, ε, Q and υ. However, for turbulent flow in a long gravity main, Swamee and Jain (1976) obtained the following solution for the pipe diameter:
For laminar flow, the Hagen–Poiseuille equation gives the diameter as:
Swamee and Swamee (2008) gave the following equation for pipe diameter that is valid under laminar, transition, and turbulent flow conditions:

## Slide 4
Example 3
As shown in figure, a discharge of 0.1 m3/s flows through a CI pipe main of 1000 m in length having a pipe diameter 0.3 m. A sluice valve of 0.3 m. (Kf = 0.15) size is placed close to point B. The elevations of points A and B are 10 m. and 5 m. respectively. Assume water temperature at 20o c. Calculate the following:
Terminal pressure h2 at point B and head loss in the pipe if the terminal pressure h1 at point A is 25 m.
The discharge in the pipe if the head loss is 10 m.
The CI gravity main diameter if the head loss in the pipe is 10 m. and a discharge of 0.1 m3/s flows in the pipe.

## Slide 5
Solution
1-
Where h2 = 23.286 m and hL= 6.714 m

## Slide 6
2- If the total head loss in the pipe is predefined equal to 10 m, the discharge in CI pipe of size 0.3 m can be calculated using this Equation for a turbulent flow:
3- the gravity main diameter for preselected head loss of 10 m and known pipe discharge 0.1 m3/s for a turbulent flow is:

## Slide 7
3- Equivalent Pipe
In the water supply networks, the pipe link between two nodes may consist of a single uniform pipe size or a combination of pipes in series or in parallel.
The set of pipes arranged in parallel and series can be replaced with a single pipe having the same head loss across points A and B and also the same total discharge Q. Such a pipe is defined as an equivalent pipe.
3-1 : Pipes in Series
Q =
;
If
Then
=

## Slide 8
Example 4
An arrangement of three pipes in series between tank A and B as shown below. Calculate the equivalent pipe diameter and the corresponding flow. Assume f=0.02 and neglect minor losses.
== 0.185 m
= 20 =

## Slide 9
3-2 Pipes in Parallel
+…
For N pipes in parallel
The discharge Q flowing in equivalent pipe is
Equating Eqs. (2) and (3) result

## Slide 10
Example 5
For a given parallel pipe arrangement below, calculate equivalent
pipe diameter and corresponding flow. Assume Darcy–Weisbach’s friction factor f = 0.02 and neglect entry and exit (minor) losses. Length of equivalent pipe can be assumed as 500 m.
=

## Slide 11
Example 6: Graph the energy line and hydraulic grade line and calculate the discharge in the pipe shown in figure.
275 m
0.9 m
E.L
H.G.L
Entrance loss
Contraction loss
Enlargement loss
hL= 9.15 m
153 m
0.6 m
244 m
0.3 m
Exit loss
Q =
Assume f1= f2 = f3 = 0.02
9.15 = + +
9.15 = 3.252 +0.77
Q = 0.232

## Slide 12
f1 = 0.022, f2 = 0.026 , f3 = 0.0204
Q = 0.204
f1 = 0.022, f2 = 0.026, f3 = 0.0205
Say ok
So, Consider Q = 0.204
For checking calculate f1 , f2 and f3 From Eq. 1
Next, for checking calculate f1 , f2 and f3 From Eq. 1
9.15 = + +
--------------(1)
9.15=3.577 + 215.714 + 0.785

## Slide 13
------- (B)
So, consider Q = 0.2088
== 0.3656 m
= 9.15 =
Or ------- (A)
Remark | Calculated f from Eq.B | Q from Eq.A | Assumed f | It.
Use f= 0.02467 | 0.02467 | 0.2320 | 0.02 | 1
Use f= 0.0247 | 0.02470 | 0.2089 | 0.02467 | 2
Ok | 0.0247 | 0.2088 | 0.02470 | 3
Another Solution :

## Slide 14: 3- Branch Piping
Branching network illustrated in Figure below is made of three elements connected to a single junction. In contrast to parallel system , no closed loops exist.
Figure: Branch piping systems: (a) gravity flow; (b) pump driven flow

## Slide 15
Example: 7
The following figure shows three reservoirs connected by pipes. Each pipe is 300 mm in diameter and 1500 m long. Assume f = 0.01 for each pipe, find the discharge in each pipe.
Assume ELj = 30 m
For pipe 1
15 =
Since Q1 ≠ Q3 and Q1 > Q3 therefore a direction of flow must be from joint j to reservoir B
Solution

## Slide 16
So, Assume flow for Q2 Such that: Q1 = Q2 + Q3 ……….. (1)
From Res. A to Res. B
= 40
From Res. A to Res. c
From Eq. (2)
From Eq. (3)
Substituting Q2 and Q3 into Eq. (1) yields
+
Solve by trial and error to find that Q1 = 0.268
So , Q2 = 0.081 from Eq.(4)
Q3 =0.1897 from Eq.(5)

## Slide 17
From Q1 = Q2 + Q3 ……….. (1)
Substituting Q1, Q2 and Q3 into Eq. (1) yields
Solve by trial and error to find that hj = 33.224
So , Q1 = 0.269 , Q2 = 0.080 & Q3 =0.1890
Another solution
From Res. A to Junction j
= 70 – hj
From Junction j to Res. B
= hj - 30
From Junction j to Res. C
= hj - 15

## Slide 18
Example: 8
In the following figure, when the pressure heads at A and B are
3.05 m and 89.9 m respectively, the pump AB adds 75 kw to the
system shown. What elevation can be maintained at reservoir D
Use the equation
D
1830 m-200mm
C=130
1520 m-150mm
C=130
1220 m-250mm
C=120
250 mm
EL=3. m
B A
P =
75 = 9.8 x Q x (89.9 – 3.05 )
Q= 0.088
For parallel pipes, Q1 + Q2 = 0.088
= 0.088
hf = 30.89 m
So, EL = 3+ 89.9 -17.46-30 89 = 44.55 m

## Slide 19
Example: 9
The water supply network shown in the following figure has pump
of power 300 kw to discharge water to the network. The pressure
developed by the pump is 20 m. Calculate the following:
1- The discharge in all pipes ()
C = 100 in all pipes.
2- Elevation at reservoir E and F
EL = 3 m
0.4
pump
E
F
B
C
A
D
337 m
800 mm
150 m
500 mm
200 m
400 mm
500 m
350 mm
0.5

## Slide 20
Power =
300 = 9.8 Qp x 20
Qp = 1.531
Line AD
=0.5 – 0.283 = 0.217
For Line AB

## Slide 21
For Line BC
Or

## Slide 22
Example: 10
The following figure shows three reservoirs connected by pipes. Find the discharge in each pipe and the piezometric head H at the junction. The fluid power input by the pump is constant equal to
For pipe 1
Solution
 | f | D (m) | L (m) | Pipe
2 | 0.02 | 0.15 | 50 | 1
1 | 0.015 | 0.10 | 100 | 2
1 | 0.025 | 0.10 | 300 | 3
 | f | D (m) | L (m) | Pipe
2 | 0.02 | 0.15 | 50 | 1
1 | 0.015 | 0.10 | 100 | 2
1 | 0.025 | 0.10 | 300 | 3
For pipe 2
For pipe 3

## Slide 23
Assume ELj = 30 m
For pipe 1
Since Q1 ≠ Q3 and Q1 > Q3 therefore a direction of flow must be from joint j to reservoir B
=
= = 1420
= = 13200
= = 62800
So, -------(1)
For pipe 3
= 0.015 m3/s
Solve Eq.(1) by trial and error to find that Q1 = 0.0736 m3/s

## Slide 24
For pipe 1
Or, …… (3)
Solve Eqs.(3, 4 & 5) by trial and error to as follows
So, Assume flow for Q2 Such that: Q1 = Q2 + Q3 ……….. (2)
For pipe 2
……….. (4)
For pipe 3 ……….. (5)
So, the solution is
Q1 = 0.054 m3/s
Q2 = 0.0322 m3/s
Q3 = 0.0214 m3/s
Hj = 43.64 m
 |  | Q2 Eq.4 | Hj Eq.3 | Assume Q1 | Iter.
- 0.0089 | 0.0227 | 0.0362 | 47.25 | 0.050 | 1
+ 0.0029 | 0.0210 | 0.0311 | 42.80 | 0.055 | 2
+ 0.0004 | 0.0214 | 0.0322 | 43.64 | 0.054 | 3
 |  | Q2 Eq.4 | Hj Eq.3 | Assume Q1 | Iter.
- 0.0089 | 0.0227 | 0.0362 | 47.25 | 0.050 | 1
+ 0.0029 | 0.0210 | 0.0311 | 42.80 | 0.055 | 2
+ 0.0004 | 0.0214 | 0.0322 | 43.64 | 0.054 | 3